## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 1
Dr Ameer Badr Khudhair

## Slide 2: Water global situation
Less than 3% of the world’s water is fresh, the rest is seawater and undrinkable.
Of this 3% over 2.5% is frozen, locked up in Antarctica, the Arctic and glaciers, and not available to man.
Thus humanity must rely on this 0.5% for all of man’s and ecosystem’s fresh water needs.

## Slide 3
The current world population is over 7.5 billion. The UN estimates that by 2050 there will be an additional more billion people with most of the growth in developing countries that already suffer water demand.
Thus water demand will increase unless everyone finds ways to conserve and recycle the precious resource

## Slide 4
3,900 children die each day due to dirty water.
1.8 million people die every year from diarrhea diseases (including cholera).

## Slide 6: Domestic and non-domestic water demand
Domestic: covers the use of water for drinking, washing, bathing, cocking and flushing, i.e. for domestic purposes.

## Slide 7
Non-domestic : covers the use of water mostly for public purposes such hospital, hotels, educational institutions, offices, commercial establishments, railway stations, airports, gardens, swimming pool and theaters.

## Slide 8: Factors influencing water demand
Population
Season
Habits and living standard
Water resources
Cost of water

## Slide 9
Water demand varies seasonally with the lowest usage in winter months and the highest usage during summer months. Variations in demand also occur with respect to time of day.
Diurnal peaks typically occur during the morning and early evening periods, while the lowest usage occurs during nighttime hours.

## Slide 10
Seasonal variations: in Summer daily water consumption rate may reach 120 to 160% of the average daily consumption rate. In Winter, daily water may reach 70%.
Daily variations: Water consumption varies from one day to another. Daily variation could reach a maximum of 130 to 170% of average daily consumption during the year or may reach a minimum value of 60%.
Hourly variations: maximum rate may reach to 150 to 225% of average daily rate at the peak.

## Slide 12
Water demand: the quantity of water that the treatment plant must produce in order to meet all water needs in the community.
Water demand includes water delivered to the system to meet the needs of consumers, water supply for fire fighting and system flushing, etc.
Additionally, virtually all systems have a certain amount of leakage that cannot be economically removed and thus total demand typically includes some leakage.

## Slide 13
Water demands expressed in gallons per day (gpd) or liters per day (lpd), can be divided by the population or Equivalent Dwelling Units (EDUs), capita.
It served to come up with a demand per person or per capita which is expressed in gallons per capita per day (gpcd), or demand per EDU (gpd/EDU).
These unit demands can be multiplied by future population or EDU projections to estimate future water demands for planning purposes.

## Slide 14
Average Annual Demand (AAD) : The total volume of water delivered to the system in a full year expressed in gallons/ liters. When demand fluctuates up and down over several years, an average is used.
Average Daily Demand (ADD): The total volume of water delivered to the system over a year divided by 365 days. The average use in a single day expressed in gallons/liters per day.
Maximum Month Demand (MMD): The gallons/ liters per day average during the month with the highest water demand. The highest monthly usage typically occurs during a summer month.
Maximum Day Demand (MDD): The largest volume of water delivered to the system in a single day expressed in gallons/ liters per day. The water supply, treatment plant and transmission lines should be designed to handle the maximum day demand.
Peak Hourly Demand (PHD): The maximum volume of water delivered to the system in a single hour. Distribution systems should be designed to adequately handle the peak hourly demand or maximum day demand plus fire flows, whichever is greater. During peak hourly flows, storage reservoirs supply the demand in excess of the maximum day demand.

## Slide 15: Flow demand and design consideration
Average daily demand = average annual demand/ 365
Maximum daily demand = average daily demand x 1.8
Peak hourly demand (max) = average hourly demand x 1.5
Water supply facilities will serve the maximum daily demand and water tanks will serve peak hour demands
Design flow for a distribution network should be based on the peak hourly demand or the peak daily demand + fire flow requirements.

## Slide 16: Fire protection requirements
Small demand annually but high demand during short period.
Can be used by this formula:
)
Where:
Q: fire requirement in l/min
P: population in thousands

## Slide 17
There is another formula to calculate the fire requirements:
F= 18 * C.
Where:
F: fire requirement in gal/min (gpm), 500< F< 8000
A: area in ft2
C: coefficient depend on the construction material, (C) for wood =1.5, fire resistance= 0.6, normal= 1

## Slide 18: Example: The average water consumption per person per day in Hong Kong is 0.13 cubic meter (130 liters). Average daily consumption of the billing period given on bill = 455 L, Number of members in the family = 4, calculate the daily water consumption, is the result below or higher the average consumption in Hong Kong?
Solution
Per capita daily water consumption of the family is
= 0.455 / 4 = 0.114 m3
= 114 Liters, which is less than the territory-wide average 130 Liters/Head/Day
Note: head = person = capita

## Slide 19
Example : A city with population of 22,000 capita has average daily demand of 600 lpcd, there is a building of ordinary construction material with each floor area of 1000 m2 and height of 6 stories, determine
Max daily demand
The fire flow demand (use the highest value)
Max flow rate during the day with 2 hours duration of fire
(1 meter = 3.28 ft, 1 gallon = 3.785 L)
Solution:
MDD = ADD * 1.8 = 600 * 1.8 = 1,080 Lpcd
Fire flow demand = 18 *C* √A = 18* 1* √ (1000*6* 3.282) = 4,573 gpm = 17,309 L/min
Fire flow demand = 4080 √ p )1- 0.01 √ p) = 4080* √22 (1 – 0.01 √22 )= 18,239 L/min
Use Fire flow demand as 18,239 L/min = 18,239 * 24*60 = 26,264,160 L/day
3. Max flow rate during the day = MDD* pop + fire flow rate during day
= 1,080 * 22,000 + 26,264,160 *2/24
= 23,760,000 + 2,188,680
= 25,948,680 L/day
= 25,949 m3/day