## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 10
Dr Ameer Badr Khudhair

## Slide 2: Disinfection
Water disinfection means the removal, deactivation or killing of pathogenic microorganisms. Drinking water disinfection has decreased the number of outbreaks of waterborne diseases, such as cholera and typhoid. Disinfectants should not only kill microorganisms. Disinfectants must also have a residual effect, which means that they remain active in the water after disinfection. A disinfectant should prevent pathogenic microorganisms from growing in the plumbing after disinfection. Disinfection has been practiced for destruction of pathogenic organisms, more particularly, bacteria of intestinal origin. The survival time of pathogenic organisms depends upon temperature, pH, oxygen and nutrient supply and resistance to toxic influences. Water disinfection does not necessarily imply sterilization (complete destruction) of all living organisms. Disinfection is used to treat both domestic water and wastewater.

## Slide 3
There are two types of disinfectants; chemical and physical:
For chemical disinfection of water the following disinfectants can be used:
Chlorine (Cl2)
Chlorine dioxide (ClO2)
Hypo chlorite (OCl-)
Ozone (O3)
Halogens: bromine (Br2), iodene (I)
Bromine chloride (BrCl)
Metals: copper (Cu2+), silver (Ag+)
Calcium permanganate (KMnO4)
Phenols
Alcohols
Soaps and detergents
Hydrogen peroxide
Several acids and bases

## Slide 4: For physical disinfection of water the following disinfectants can be used:
Ultraviolet light(UV)
Electronic radiation
Gamma rays
Sounds
Heat
Pressure

## Slide 5: The characteristic of a good disinfectant are:
Effective kill of pathogenic microorganisms
Nontoxic to humans or domestic animals
Nontoxic to fish and other aquatic species
Easy and safe to store , transport and dispense
Low cost
Easy and reliable analysis in water
Provides residual protection in drinking water

## Slide 6: Chlorine (Cl2)
Chlorination is commonly used for disinfection. Chlorine can be added as a gas or as a liquid. If it is added to the water as a gas, it is stored as a liquid, which vaporizes around -31°F. Liquid chlorine is the primary form used since it is less expensive than calcium hypochlorite solid (Ca(OCl)2) and sodium hypochlorite (NaOCI). When chlorine gas dissolves in water, it forms hydrochloric acid (HCl) and hypochlorous acid (HOCl). Chlorine is corrosive and toxic. Special safety and handling procedures must be followed with its use.

## Slide 7
Chlorine is shipped in liquid form, in pressurized steel cylinders ranging in size. The moist gas is corrosive and so all piping and dosing equipment must be nonmetal or resistant to corrosion. Use of chlorine in various stages of treatment, and even in raw water collection and potable water distribution system, is common practice. Multiple or split chlorination schemes frequently enhance the efficiency of many other unit water treatment processes. In practice, the terms plain-chlorination (simple chlorination), pre-chlorination, post-chlorination, and re-chlorination are commonly used to specify the location at which chlorine is applied.
Plain or simple chlorination represents the sole public health safeguard. It involves the application of chlorine to water that receives no other treatment. When applied to impounded or naturally elevated surface supplies. Post chlorination follows filtration for disinfection and for provision of free or combined residual chlorine in a part or the entire distribution system. Re-chlorination is common where the distribution system is long and complex and where the plant effluent residual is insufficient to control bacterial and algal re-growth.

## Slide 8
Figure 1: break point chlorination

## Slide 9
Figure 2: chlorination tank

## Slide 10: Ozone as a Disinfectant
Ozone is a strong oxidizing gas that reacts with most organic and many inorganic molecules. It is more reactive than chlorine. It does not react with water to produce disinfecting species but decomposes in water to produce oxygen and hydroxyl free radicals. Since it does not produce a disinfecting residual, chlorine is added to treated potable water before distribution for a protective residual. The half-life of ozone in water is approximately 10 to 30 min and shorter if pH is above 8 and hence it must be generated at site. Ozone is rarely applied solely for disinfection because of the high cost relative to chlorine. Ozone does not produce any health-related by-products and for this reason there is increased interest in application of ozone in potable water treatment. Ozone has multiple possibilities in water treatment. It oxidizes cyanide, iron, manganese and, organic matter including bacteria and viruses.

## Slide 11
Dose: Concentration of disinfectant added, mass per liter of water.
Residual: Concentration of disinfectant remaining and therefore available to combat existing or subsequent microbial contamination.
Demand: Difference between dose and residual.
Breakpoint chlorination is the point where the demand for chlorine has been fully satisfied in terms of chlorine addition to water.

## Slide 12: Example 1: determine the break point dosage of chlorine given the data below which was obtained from a chlorination experiment.
Dosage (mg/l) | 1 | 2 | 3 | 4 | 5 | 6 | 7
Reactive chlorine (mg/l) | 0.2 | .45 | 1.05 | 2.75 | 4.5 | 5.15 | 6.05
Dosage (mg/l) | 1 | 2 | 3 | 4 | 5 | 6 | 7
Residual chlorine (mg/l) | 0.8 | 1.55 | 1.95 | 1.25 | 0.5 | 0.85 | 0.95

## Slide 13
Chart: Dosage (mg/l)
| 1 | 2 | 3 | 4 | 5 | 6 | 7
 | 0.8 | 1.55 | 1.95 | 1.25 | 0.5 | 0.85 | 0.95

## Slide 14: Example 2: For wastewater consists of ammonia, organic matter and microorganisms), draw breakthrough curve using following information and calculate chlorine dose to achieve 0.75 mg/l free available chlorine.
Chlorine dosage (mg/l) | 0.1 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3
Chlorine residual (mg/l) | 0 | 0.4 | 0.8 | 0.4 | 0.4 | 0.9 | 1.4

## Slide 15: From figure; break point is 2 mg/l To get 0.75 mg/l from available chlorine; Then chlorine dose required = 2+ 0.75 = 2.75 mg/l
Chart: Chlorine dosage (mg/l)
| 0.1 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3
Chlorine residual (mg/l) | 0 | 0.4 | 0.8 | 0.4 | 0.4 | 0.9 | 1.4

## Slide 16
Where:
C: the concentration of disinfectant
N: concentration of organisms
K: Chick’s law rate constant, 1/time
t: time, second

## Slide 17: Example 3: Calculate the remaining percentage of pathogens after 1 minute of disinfection with K=0.046/min, use Chick’s Law. / = exp (-k.t) = exp (-0.046/min×1 min) N= 0.9550 *100 = 95.5%