## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 5
Dr Ameer Badr Khudhair

## Slide 2: Rapid mix
Rapid mix, or flash mix or quick mix is the process by which a coagulant is rapidly and uniformly dispersed through the mass of the water. The process usually occurs in a small basin immediately preceding or at the head end of the ‘coagulation basin’. This process is used to generate a homogeneous mixture of raw water and coagulants which result in the destabilization of the colloidal particles in the raw water to enable coagulation. Mixing is provided by pumps, venture flumes, air jets or rotating impellers (paddles, turbines, or propellers). Where possible, the rapid mix should be a two-compartment unit.

## Slide 3: Mixing types
Hydraulic mixing: such as Baffle mixing, mixing using obstacles. Head loss between 0.5- 1m.
Air mixing: by using compressed air, at the same time of mixing oxygen react with iron (Fe+2) and Manganese (Mn+2) pollutants that exist in the raw water.
Mechanical mixing: use propellers, turbines paddles. It is more efficient than other mixing type.

## Slide 4: Design parameters
Detention time: 30- 60 sec
Basin dimensions: 3 – 10 ft
Mixing intensity: 700- 100 1/sec
Power: 0.25 – 1.0 hp/MGD

## Slide 5
Example: design a rapid mixing unit for discharge 5 Million gal/day, use 2 units, cubic shape.
Solution:
If detention time is not mention then use t = 60 sec
Volume=Q.t = 5* 106*3.785/(24*60*60)*60=13.142 m3
2 units; the volume for each unit = 13.14/2 = 6.57 m3
The unit has cubic shape
Height = (volume)1/3 = 1.87; use 2 m
Add 0.5 m for safety
H = 2 + 0.5 = 2.5 m
Length = width = 2 m

## Slide 6: Coagulation
Coagulation is the widely used process to remove the substances producing turbidity in water. Coagulation is a chemical process in which particle charge is satisfied while flocculation is a physical process which agglomerates particles that are too small for gravity settling so that they may be successfully removed during the sedimentation process. Coarser components such as sand and silt can be removed from water by simple sedimentation. Finer particles such as colloidal matter and finely divided suspended matter cannot be removed from water by plain sedimentation in tanks having ordinary dimensions. So they must be flocculated to produce larger particles that are settleable. The process of coagulation may find use in the softening of hard water with lime or lime and soda ash and removal of color producing substances such as colloidal metallic hydroxides or organic compounds having a much smaller particle size.

## Slide 7: Coagulation treatment depends upon many factors such:
Water quality
Water quantity
Chemical composition of the water
Temperature
pH
Mixing conditions
Turbidity
Type of coagulant
detention time

## Slide 8
Coagulation should be carried out within the optimum pH range for the particular water. For certain waters it may be necessary to adjust the pH with acid, or lime, or soda ash, etc. The selection of type and dosage of the chemical coagulant must be made by experimentation, most commonly with jar tests. Commonly used coagulants (table 1) include those which are iron or aluminum-based, lime, and polymers. Aluminum sulfate, commonly known as alum, is effective for pH values of 5.5 to 8.0.

## Slide 9
Table 1: some of commonly used coagulants

## Slide 10: The reason for using Alum frequently in Iraq
Low cost
Easy to store (do not oxidize in the air) and transport.
Available
Can used as solid or fluid
Keep its properties over time

## Slide 11: Coagulants shape
Dry feeding: powder or grains
Wet feeding : liquid

## Slide 12: Jar test
This test represents coagulation and flocculation processes but in small scale. It is used to find the optimum dose. It is divided into three steps:
Rapid mix (1- 2 minutes) the coagulation process starts.
Slow mix (20 minutes) the flocculation process starts
Settling Without mixing (30 -40 minutes) to settle the flocs.
Then measuring the water turbidity and draw a chart then find the optimum dose of coagulant.

## Slide 13
Figure 1: Jar test device

## Slide 14
Example: Find the quantity of alum used per day. The dose of alum = 5 mg/l and Q =100 m3/day.
Total quantity = Q* dose
=100* 5 = 500 g/day = 0.5 kg/day

## Slide 15
Example: Find out the quantity of alum required to treat 18 million liters of water per day. The dosage of alum is 14 mg/L. also work out the amount of CO2 released per liter of treated water.
Solution:
Quantity of alum/day = 14*18 = 252 kg
The chemical reaction is as follows:
Al2(SO4)3.18H2O + 3Ca(HCO3)2 2Al(OH)3 + 3CaSO4 + 18H2O + 6CO2
Molecular wt. of Alum = 2* 27+3(32+16*4) + 18(1*2+16) = 666 g/mol
Molecular wt. of CO2 = (1*12)+(2*16) = 44 g/mol
666 mg of alum release 6*44 mg of CO2
The amount carbon dioxide would release per day = (6*44/666)* 14*18 =100.8 kg of CO2/day