## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 6
Dr Ameer Badr Khudhair

## Slide 2: Flocculation
During flocculation, slow-moving paddle mixers gently stir a mixture of water and coagulant to generate floc. A series of flocculation chambers is usually employed rather than a single basin. The common mechanical mixing devices are paddle flocculators, flat-bed turbines, and vertical-turbine mixers. These mixing devices are shown in figure below. Flocculation chamber is built as close to sedimentation tank as possible.

## Slide 3
Type of flocculator:
Mechanical flocculator; horizontal or vertical
Hydraulic flocculator

## Slide 4: Design criteria
Detention time (20-30) minutes
Velocity gradient G (20 -50) 1/sec;
GT =G.T; 20,000 - 200,000
P: power input (watt); w=N.m/s; P= 0.5* Cd.ρ.A.v3
Cd: drag coefficient, depend on liquid type and surface roughness.
ρ: water density (1000 kg/m3)
A: total area of paddles
v: relative velocity; v= absolute velocity (vi)- velocity of water in paddles
v = (1-k)* 2π.r.n/60
vi: (rpm), m/s, vi =2π.r.n/60
r: effective radius (m)
n: rpm
k: relative velocity between water and abs velocity of paddles
k=velocity of water in paddles/ abs velocity (vi)
μ: dynamic viscosity (N.s/m2), (Pa · s); if not mentions in the question use (1.312* 10-3 N.s/m2)
V: floccualtor volume (m3)

## Slide 5
Example: For a flocculator tank, the following data are given: Q =300 m3/min, D.T. =20 min, P =2KW/unit of flow, L= 3D, W =2D, D =depth of the tank, v=75% vi peddles, ρ =1000 kg/m3, Cd =1.2, find:
1. L, W, D of the flocculator tank.
2. Total area of paddles knowing that three rows are used in this flocculator along its length and the area for one row is 10% W.D.
3. RPM of the paddles in flocculation tank. Use r = 4.5 m
Solution:
Volume = Q*D.T. =300*20 = 6000 m3
Volume = L.W.D = 3D. 2D.D= 6D3; D =10 m; w = 20 m; L =30m
Area of one raw of paddles is equal to W*D =200 m2
Area of one paddle = 10% (W*D) =10*200/100 = 20m2
Total area of paddles =3*20 =60 m2
P= 0.5* Cd.ρ.A.v3
P=2kw for each unit of flow
P total= 2*300 = 600 kw = 600,000 watt
v= 2.56 m/s
v =0.75*vi; vi = 3.413 m/s
vi =2π.r.n/60; r = 4.5 m
n=7.24 rpm

## Slide 6
Example: A flocculator with L=8m, w =10m, depth =6m and designed with one rotating paddle of blades as shown in figure below. Knowing that D.T. =20 min and cd =1.2, µ =1.3 cp, rpm =2, ρ =1000 kg/m3, v =0.75*vi, find: (1 cp = 10−3 Pa·s = 1 mPa·s) (cp= centipoise). Power input in N.m/sec; G in 1/s

## Slide 7
Solution:
P= 0.5* Cd.ρ.A.v3
There are two blades
A1= 0.3*8*2= 4.8 m2
A2=0.2*8*2 =3.2 m2
r1= 3.6/2 =1.8 m; r2= 2/2=1 m
vi =2π.r.n/60
vi1= 2*3.14*2*1.8/60 =0.377 m/s
vi2= 2*3.14*2*1/60 = 0.21 m/s
v = 0.75 vi, vi = vp
v1=0.75*0.377 = 0.282 m/s
v2=0.75*0.21 =0.157 m/s
p =0.5*1.2* 1000* (A1.v13+A2.v23) = 72 N.m/sec
= (72/ (1.3*10-3)*(10*8*6))0.5 = 10.74 s-1
Not in range (20 – 50) sec-1 then not ok.

## Slide 8
Example: A flocculator tank is designed to treat 1 m3/sec have a length 30 m and 12 m width and 4.5 m depth, it is equipped with paddles 0.3m width and 12m length, which are set in pins on four shafts rotation =2.5 rpm. The shafts are at the mid depth of the tank and the distance from the half to the center line of paddle is 2 m. The ratio between water velocity and paddle velocity is one quarter, take viscosity =1.312* 10-3 N.s/m2, find: detention time, power input, G and G.T.

## Slide 9
Solution:
Volume= 30*12*4.5 =1620 m3
D.T.= Vol./Q =1620/ 1 =1620 sec = 27 min
P= 0.5* Cd.ρ.A.v3
If Cd is not mention in the question use 1.8
No. of paddles = 2*4 =8 paddles
A total = area of one paddle* no. of paddles = 0.3*12*8 =28.8 m2
v =(1-k)*2π.r.n/60 = (1- 0.25)*2*3.14*2*2.5/60 = 0.392 m/s
P= 0.5* 1.8*1000 *28.8*(0.392)3 = 1561.3 watt
=27.1 sec-1 , G =20-50 sec-1 ; then ok
G.T = G. D.T =27.1* 1620 = 4.3902 * 104; GT = (2* 104- 2*105); then ok