## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 7
Dr Ameer Badr Khudhair

## Slide 2: Sedimentation / clarification tank
Sedimentation or clarification is the process of removal of particulate matter, chemical floc, and precipitates from suspension through gravity settling. The removal of particulate matter is accomplished in settling tanks (also called sedimentation tanks or sedimentation basins, or settling basins or clarifiers). Water clarification is a vitally important step in the treatment of surface waters. Poor design of the sedimentation basin will result in reduced treatment efficiency that may subsequently upset other operations.

## Slide 3: Types of Sedimentation Tanks
The effectiveness of a sedimentation tank depends on the settling characteristics of the suspended solids that are to be removed and on the hydraulic characteristics of the sedimentation tank. The hydraulic characteristics depend on both the geometry of the tank and the flow through the tank. Most sedimentation tanks are of the horizontal-flow type which may be either rectangular or circular in plan and are constructed of reinforced concrete. Unless sludge is removed continuously, allowance must be made in the basin volume for sludge accumulation between cleanings.

## Slide 4
Figure 1: circular settling tank

## Slide 5
Figure 2: rectangular settling tank

## Slide 6
Sludge Collection - Most sedimentation tanks are provided with sloping bottoms to facilitate the removal of deposited sludge. Sedimentation basins may be equipped with sludge collection and removal mechanisms to maintain volumetric efficiency and reduce the need to shut down for cleaning. Circular tanks may be provided with rotating mechanisms driven by motors mounted at the center of the tank. The rotating apparatus (equipped with blades that travel slowly around an axis just above the floor of the basin) is designed to push the sediment to the center to facilitate the movement of the sludge.
For rectangular tanks, the bottoms are usually designed to slope from the effluent end of the tank to a sludge hopper located at the tank inlet. The main collector will include a drive unit which motivates a set of continuously moving scrapers that serve to move the sludge to the hopper.

## Slide 7: Principle of sedimentation
The sedimentation of discrete spherical particles may be described by Newton’s Law, from which the terminal settling velocity is found to be:
Where:
v= terminal settling velocity
= mass density of the particle
= mass density of the fluid
g = acceleration due to gravity
d = diameter of the particle

## Slide 8
= a dimensionless drag coefficient defined by
Where:
= Reynolds number,
= absolute viscosity of the fluid.
for ≤ 0.5 (laminar)
for 0.5 ≤ ≤ 10,000 (transition)
For small RN use stokes’ law
Stokes’ law

## Slide 9
Dynamic viscosity μ
poise(P), Pascal (Pa)* sec
1 P = 0.1 Pa·s= 0.1 kg·m−1·s−1
1 cP = 1 mPa·s = 0.001 Pa·s = 0.001 N·s·m−2 = 0.001 kg·m−1·s−1.
Kinematic viscosity ν
m2/s, stokes (St)
1 St = 1 cm2·s−1 = 10−4 m2·s−1.
1 cSt = 1 mm2·s−1 = 10−6 m2·s−1.

## Slide 10: Settling tank zones
Zones in Settling Tanks – Settling tanks have been traditionally divided into four zones for purposes of discussion, each zone having its characteristic function. See Figure below.
Figure 3: settling zone

## Slide 11
Inlet zone provides a smooth transition from the influent flow to the uniform and steady flow desired in the settling zone. Outlet zone provides a smooth transition from the settling zone to the effluent flow. Sludge zone receives the settled material and prevents it from interfering with the sedimentation of particles in the settling zone. Settling zone provides tank volume for settling, free from interference from the other three zones.

## Slide 12
Example 1: Calculate the terminal settling velocity for a sand particle in water at 10˚C. Assume the sand particle has a diameter of 25 µm and a density of 2650 kg/m3 (s.g =2.65). For water at 10˚C, Kinematic viscosity= 1.306 *10-6 m2/s.
Vs=((9.81*(2650-1000)*(25*10-6)2/(18*1000*1.306*10-6))*3600 = 1.55 m/h
Verify flow conditions. Check the Reynolds number to see if the particle is settling under laminar conditions and if the terminal velocity calculated in previous step is valid.
Re = 1000*(25*10-6)(1.55/3600)/(1.306*1000*10-6) = 0.0082
Comment: the Reynolds number is much less than 0.5; consequently, laminar law exists and stakes' law applies.

## Slide 13
Q =v.A =v.h.w
v= Q/w.h
=
As = w.L

## Slide 14
SOR: Surface Overflow Rate, which is numerically equal to the flow divided by the plan area of the basin, but which physically represents the settling velocity of the lowest settling particle which is 100% removed.

## Slide 15
Example: Design a settling tank (coagulation-sedimentation) with continuous flow for treating water for a population of 48,000 persons with an average daily consumption of 135 lpc. For sedimentation take detention period of 3 hr, depth =3m, width = 12m and slope of bed = 1/60.
Solution:
Average daily consumption =135 *48,000= 6,480,000
Maximum daily consumption = 6,480,000 *1.8 = 11,664,000 L = 11,664 m3
Capacity of tank = 11,664,000 * 3/24 =1458 m3
Depth is 3m
Sectional area of settling tank = 1458/ 3 =486 m2
Width is 12 m
Length of tank = (486/ 12) =40.5 m
Provide 30 cm extra depth or sludge storage
Depth at inlet end = 3 + 0.3 =3.3 m
Depth at outlet end = 3.3 + (40.5/60) = 3.975 m (slope of bed = 1/60)

## Slide 16
Note: The floc chamber at the entry should be provided in addition to 40.5 m length. Its depth may be assumed 2.5 m and the period of flocculation may be taken as 30 min. The capacity of flocculation chamber is 1/6 of that of settling tank. (1458/6)
Sectional area =1458/(6*2.5) = 97.2 m2
Provide width same as of settling tank =12 m
Length of tank = 97.2/ 12 =8.1 m
Thus floc chamber will be 12*8.1*2.5 m

## Slide 17
Example 2: Rectangular settling tank of continuous flow type having surface area of 240 m2, the flow rate is 1.6 m3/s. Calculate the SOR (Surface Overflow Rate) with which the particles will be completely removed.
Solution:
SOR= Q/As = 1.6/240 =0.0067 m/s
Hence all the particle having v ≥ 0.0067 m/s will be completely removed

## Slide 18
Example 3: A clarifier with an area of 150 m2 treat 3000 m3/d contain a clay grains with particles density of 1.05 gm/cm3 and diameter 0.055mm, what is the percentage of particles will be removed in the clarifier? µ =1.08*10-3 N.s/m2.
= 3000/150 = 20 m/d = 0.0002314 m/sec
=9.81(1050-1000)*(0.055/1000)2/(18*1.08*10-3) = 0.00007632 m/sec
= 0.00007632/0.0002314*100 = 32.98%

## Slide 19
Example 4: Removal of discrete particles, a settling basin is designed to have a surface overflow rate of 32.6 m/day. Determine the overall removal obtained for a suspension with the size distribution given. The density of the particles is 1.2 g/cm3 and the water temperature is 20˚C. At 20˚C, µ =1.027 N.s/mm, ρ =0.997 g/cm3
particles size (mm) | 0.1 | 0.08 | 0.07 | 0.06 | 0.04 | 0.02 | 0.01
weight fraction greater than size% | 12 | 15 | 40 | 70 | 93 | 99 | 100

## Slide 20
Fraction with settling velocity less than stated | 88 | 85 | 60 | 30 | 7 | 1 | 0
v (mm/s) | 1.08 | 0.69 | 0.53 | 0.39 | 0.17 | 0.04 | 0.01
Re | 0.1045 | 0.0535 | 0.0358 | 0.0226 | 0.0067 | 0.0008 | 0.0001
SOR = 32.6 m/day = 0.37 mm/s, Xs =27%
Chart: v (mm/s)
| 1.0761657470518231 | 0.68874607811316679 | 0.52732121605539339 | 0.38741966893865626 | 0.1721865195282917 | 4.3046629882072925E-2 | 1.0761657470518231E-2
 | 88 | 85 | 60 | 30 | 7 | 1 | 0

## Slide 21
dx | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03
v | 0.06 | 0.16 | 0.22 | 0.26 | 0.3 | 0.34 | 0.37
vdx | 0.0024 | 0.0064 | 0.0088 | 0.0104 | 0.012 | 0.0136 | 0.0111
1-Xs= 1- 0.27 = 0.73
0.0647
= 90.5%

## Slide 22: The design criteria for the sedimentation tanks
SOR = 20 to 40
D.T (detention time) = 2 to 4 hours
Depth of tank = 3 to 6 m
L/W = 4/1 to 2/1
Length for rectangular sedimentation tank; L≤ 40 m
Diameter of circular sedimentation tank; D ≤ 40 m
For design minimum of two basins must be provided.
Weir loading = 120 to 250

## Slide 23
Example 5: Design a rectangular sedimentation tank/ tanks for Q =120,000 m3/day. SOR = 30 m3/m2.day, D.T =4 hours, L =40, L/w =4/1.
Solution:
As =Q/SOR = 120,000/ 30 = 4000 m2
For the big area and limitations, choose many tanks
w =40/4 =10 m
As for one tank = w*L =10*40 =400 m2
No. of tanks = 4000/400 =10
Volume of tank =Q* D.T =120,000*4/24 = 20,000 m3
Depth of tank = Vol./As =20,000/4000 =5 m

## Slide 24
Example 6: A rectangular settling tank without mechanical equipment is to treat 2,400,000 lpd of raw water. The sedimentation period is to be 4 hrs, the velocity of flow 10 cm/minute and the depth of the water and sediment is 4 m. If an allowance of 1.2 m for sediment is made, what should be the:
a) Length of the basin
b) Width of the basin.
Detention period = 4 hrs = 240 minutes
Flow velocity = 10 cm/min
Required length = (240*10)/100 = 24 m
Volume of water to be treated in each 4 hr period = (24,00,000*4)/ 24 = 400,000 L =400 m3
Length of basin = 24m
Cross sectional area of basin = (400/24) = 16.7 m2
Depth of water when 1.2m is sediment = 4 - 1.2 =2.8 m
Required width of the tank = 16.7/2.8 =5.95 , say 6 m
Size of settling tank 6* 24 * 4m
If 30 cm is taken as free board depth of the tank will be 4.3 m

## Slide 25
Example 7: A circular sedimentation tank with a central of 4 m in diameter is to be treat 75 m3/h raw water and the detention time is 2h, find: (1N.s/m2 =1000c.p)
The diameter and depth of tank
Weir loading in (m3/m.d)
The diameter of smallest settling particle to be removed if SOR =1.2 m/hr, ρs =2 gm/cc, ρw =1.0 gm/cc, µ=1.3 centi poise
As = 3.14*dout2 /4 - 3.14*din2/4 = 3.14/4(d2-16)
SOR = Q/As
1.2 =75/(3.14(d2 -16)/4)
Diameter =10 m
Depth = 2.4 m
Weir loading =75/(3.14*4) = 5.96 m3/m.h
1.2/3600 = 9.81*1000*(2-1).d2/ (18*1.3/1000)
d= 0.028 mm

## Slide 26
Example 8: Given two sedimentation tanks have same discharge and SOR, detention time 2.5 h, the rectangular tank dimension (50*25*5), find:
The diameter of the circular tank
The settling velocity of the particles for 50% removal
For rectangular tank
Q= vol./ time = 5*25*50/2.5 =2500 m3/h
SOR =Q/As =2500/(50*25) =2 m/h
For circular tank
SOR =Q/As
2= 2500/(3.14(D2-12)/4)
D= 40 m
vs = 0.5* 2 =1 m/h