## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 8
Dr Ameer Badr Khudhair

## Slide 2: Filtration
Water filtration is a physical and chemical process for separating suspended and colloidal impurities from water by passage through a porous medium
A bed of sand or other granular material.
Water fills the pores of the medium, and the impurities are left behind in the openings or upon the medium itself.

## Slide 3: Type of Filters
Slow Sand Filters: This type of filters was the one used first in water treatment.
One of the principal drawbacks is the large land areas required.
These filters are usually covered to protect against freezing in winter and algae growth in summer.
Slow sand filters remove most suspended solids and reduce bacteria in excess of 98 percent.
The under drainage system is constructed from split tile, with laterals laid in coarse stone and discharging into a tile or concrete main drain.
The length of run between cleanings is 20 – 60 days.
Many slow sand filters have no pretreatment and others are preceded by coagulation, settling, or roughing filters.
Slow sand filters are cleaned by scraping a surface layer of sand and washing the removed sand, or washing the surface sand in place by a traveling washer.
Figure 1 shows a typical slow sand filter.

## Slide 4
Figure 1: Slow sand filtration basin

## Slide 5
Gravity Rapid Sand Filters: The vast majority of present-day water treatment plants use the gravity rapid sand filter.
This filter is normally a single-media, down flow, fine-to-coarse filter.
Natural silica sand is the common filtering medium, but crushed anthracite coal is also widely used.
The size of the sand and the depth of the bed determine the velocity of applied wash water and the height of the gutter edge above the sand surface.
Filters containing coarse sand must be deeper than those containing fine sand, and require a greater velocity of applied wash water to lift the sand and clean the bed properly.
Disadvantages of rapid sand filters as compared to slow sand filters include surface blockage, breakthrough due to coarse media, and loss of biological treatment due to high-rate backwashes.
Figure 2 shows a typical section of a rapid sand filter.

## Slide 6
Figure 2: section of a rapid sand filter.

## Slide 7
Pressure Filters: Pressure filters are based on the same principles as rapid sand gravity filters, except that the filter is contained in a pressure vessel, usually a cylindrical steel tank.
Granular filter media is used.
Water is pumped under pressure through the filter, and the media are washed by reversing flow through the bed, flushing out the impurities.
Filtration rates are comparable to those in gravity rapid sand filters.
The maximum head loss can be significantly greater since it is a function of the input pump pressure rather than static water level.
Careless operation is a problem because of the fact that the bed cannot be seen, and excess pressure can be applied to force water through the filter.
Pressure filters are commonly installed in small municipal softening and iron-removal plants, and in industrial water treatment processes.
Figure 3 illustrates a typical pressure filter.

## Slide 8
Figure 3: section of typical pressure filter.

## Slide 9
Table 1: Show the difference between Rapid sand filter (RSF) and Slow sand filter (SSF)
 | Rapid sand filter (RSF) | Slow sand filter (SSF)
Space | Occupies little space | Large space
Rate of filtration | High: 100 times faster than SSF | Low
Effective sand size | 0.4-0.7 mm | 0.2 – 0.3 mm
Preliminary treatment | Coagulation and sedimentation | Plain sedimentation
Washing | Back washing | Scraping the sand
Loss of head allowed | High | Low
Removal of turbidity | Good | Good
Removal of color | Good | Fair
Removal of bacteria | 98 – 99% | 99.9 – 99.99%
Operation | Require expert supervision | No need for expert
Cost of operation | Capital cost is low; running cost high | Capital cost is high; running cost low
Common applications | Small ground water systems | Most commonly used filter for surface water treatment