## Slide 1: CE 405 Sanitary and Environmental Engineering
Al Mansour University College
Civil Engineering department
2017-2018
Lecture 9
Dr Ameer Badr Khudhair

## Slide 2: Design criteria of Filters
Rapid filtration rate = 120 – 240 m/day
Slow filtration rate =1.2 – 2.4 m/day
Number of filters = 0.044.Q0.5 (Q: m3/day)
Total surface area =
/W = 1 to 1.4
water would be required to back wash = number of filters washed × amount of water needed for one filter
water quantity for washing = filtration rate* time* area of one filter

## Slide 3
Example 1: Design a slow sand filter for a community of 40,000 capita, the perspective water consumption is 200 lpcd. The filtration rate is 2.4 m/day.
Maximum demand =1.8* 200*40,000/1,000 =14,400 m3/day
Area of filter = 14,400/2.4 = 6,000 m2
Number of filter = 0.044*Q0.5
=0.044*14,4000.5 =5.28; approximate to 6 basins
Area of one unit/ basin = 6000/6 =1000 m2
Each unit of 31.7 * 31.7 m

## Slide 4
Example 2: Design a rapid sand filter to treat water for 240,000 capita, town being supplied water at the rate of 200 lpcd. The filtration rate is 100 L/(m2.min).
Quantity of water to be treated = 240,000*200*1.8/1000 = 86,400 m3/day
Filtration rate = 100 L/(m2.min) = 144 m/day
Filtration area = 86,400/144 = 600 m2
No. of filters = 0.044*Q0.5 =0.044*(86,400)0.5 = 12.9 ; approximate to 12 units
Area of each unit =600 /12 =50 m2
Each unit of 7.1 * 7.1 m

## Slide 5
Example 3: A filter has an area of 36m2. If it is washing for 5 min at the rate of 60 cm per minute, how much wash water will be required?
Water quantity for washing = rate* time* area of one filter
= 60 cm/min * 5 min * 36m2 /100 = 108 m3

## Slide 6
Example 4: A rapid sand filter operating at 90 liter/m2/min needs washing after 24 hours of operation. Using the information in previous example, what percent of water that is filtered will be required as wash water?
Total water filtered in a day = 90*36*60*24 = 4,665,600 liter
Water required for wash (as in previous example) = 108,000 liter
Percentage of wash water =108,000/4,665,600 *100 = 2.3%

## Slide 7
Surface area =Q/ filtration rate = 23,000/120 =192 m2
No. of filters = 0.044*Q0.5 =0.044*(23000)0.5 = 6.67 = 6
Area of filters = total area/ no. of filters = 192/6 =32 m2
When one filter is not working then;
No. of working filters = 6 -1 = 5
Total area = 5* 32 =160 m2
Filtration rate = Q/As = 23000/160 = 143.75 m/day < 180 m/day …ok
When one filter is not working and one filter is backwash then;
No. of working filters = 6 -2 = 4
Total area = 4* 32 =128 m2
Filtration rate = Q/As = 23000/128 =179.7 m/day < 240 m/day …ok
Water quantity for washing for one filter = rate* time* area of one filter
= 1 *10*32 = 320 m3
Example 5: A rapid filter plant is designed to treat 23,000 m3/day of a rate of 120 m/day.
Determine the size and number of units required if the filtration rate is not to be exceeded 180 m/d with one filter being back washed.
240 m/day with one filter out of service and one filter being back washed.
How much water would be required to back wash one filter if the wash is 1 m/min and continues for 10 min?

## Slide 8
Example 6: Find the number of rapid gravity filter units so as to treat 20 million liters per day, assuming that the filter may be washed twice a day and duration of each washing is 15 minutes.
Design the filter bed for the unit proposed and the quantity of wash-water required for washing of each unit?
Note: The rate of filtration of rapid gravity filter = 5000 L/m2/hour and proposing small size unit of 17.5 m2 area, use 4 units as a stand by units.
Design of filter bed
Per day working of filter bed =24 hours - 2*15 min =23.5 h
Then one unit of filter gives quantity of water in one day = 5000*17.5*23.5 = 2,056,250 L/day
Number of unit required = (20* 106)/2,056,250 =9.7 = 10 units
Provide 14 units of rapid gravity filter where 4 units are as stand by units
Quantity of wash water
Water quantity for washing one unit = rate* time* area of one filter
= 5000/1000 *0.5*17.5 = 87.5 m3

## Slide 9
There are many equations that may be used in the calculation of head loss in filtration beds such as:
Carmen – Kozen equation:
Fair and Hatch equation:
Rose equation:
Head loss in filtration bed

## Slide 10
Where:
H: head loss (m)
F: friction factor
Ø: shape factor, the highest value is 1, it depend on the shape of media particle
α: porosity, it depend on void ratio in media
L: length of filtering media (thickness)
d: diameter of the grains
v: filtration rate
Re: Reynolds No.
ʋ: kinematic viscosity
S: shape factor, in Fair equation, range from 6 to 7.7
Cd: drag coefficient, Cd= 24/Re +3/Re 0.5 +0.34

## Slide 11
Example 7: Determine the head loss in a filter bed composed of 30cm of uniform anthracite with an average size of 1.6 mm and 30 cm of uniform sand with average size of 0.5 mm for filtration rate of 160 l/m2.min. Assume that the operating temperature is 20˚C, use Rose equation. Assume φ=1, α= 0.4, µ=1.003*10-3 pa.s
For anthracite
v= 160/1000/60 =2.67*10-3 m/s
Re= (1000* 2.67*10-3 *1.6/1000)/ 1.003*10-3 = 4.26
Cd= 24/Re +3/Re 0.5 +0.34 =(24/4.26 )+(3/4.260.5)+0.34 = 7.43
= 0.042 m
For sand
Re= (1000* 2.67*10-3 *0.5/1000)/ 1.003*10-3 = 1.33
Cd= 24/Re +3/Re 0.5 +0.34 = (24/1.33 )+(3/1.330.5)+0.34 = 20.08
= 0.365 m
Total loss = anthracite head loss + sand head loss = 0.042+ 0.365 = 0.407m